## Sheet2
STATIC PRESSURE CALCULATOR
| TO FIND DUCT DIAMETER AND FRICTION LOSS |  |  |  |  | TO FIND DUCT DIAMETER AND DUCT VELOCITY |  |  |  |  | TO FIND DUCT VELOCITY AND FRICTION LOSS
| Enter Velocity, Air Flow & Length |  |  |  |  | Enter Friction Loss, Airflow & Length |  |  |  |  | Enter Friction Loss, Airflow & Length
Available Pressure - (Inches W.C.)
|  |  | Duct Velocity (FPM) |  | 6600 |  |  |  |  | 0.23 |  |  |  | Duct Diameter Round (inches) | 12
|  |  | Duct Airflow (CFM) |  | 8000 |  |  |  | Duct Airflow (CFM) | 1000 |  |  |  | Duct Airflow (CFM) | 1000
|  |  | Duct Length (Feet) |  | 50 |  |  |  | Duct Length (Feet) | 100 |  |  |  | Duct Length (Feet) | 100
| Enter Number of Bends |  |  |  |  | Enter Number of Bends |  |  |  |  | Enter Number of Bends
|  |  | 45º Bends (QTY) |  | 0 |  |  |  | 45º Bends (QTY) | 0 |  |  |  | 45º Bends (QTY) | 0
|  |  | 90º Bends (QTY) |  | 0 |  |  |  | 90º Bends (QTY) | 0 |  |  |  | 90º Bends (QTY) | 0
|  |  | 180º Offset (QTY) |  | 0 |  |  |  | 180º Offset (QTY) | 0 |  |  |  | 180º Offset (QTY) | 0
| Results |  |  |  |  | Results |  |  |  |  | Results
|  |  | Duct Diameter (in) |  | 14.9 |  |  |  | Duct Diameter (in) | 11.8 |  |  |  | Duct Velocity (FPM) | 1273.8854
Friction Loss - (Inches W.C.)
|  | Friction Loss - (Inches W.C.) |  |  | 2.2176 |  |  |  | Duct Velocity (FPM) | 1317.4339 |  |  |  |  | 0.21637
| TO FIND AIR MIXTURE |  |  |  |  | TO FIND EQUIVALENT RECTANGULAR DUCT |  |  |  |  | TO FIND EQUIVALENT ROUND DUCT
[6 empty] | Enter Diameter |  |  |  |  | Enter Height
|  |  | First Airstream | [5 empty] | Round Duct Diameter (in) | 12 |  |  |  | Rectangular Duct Height (in) | 8
|  | 0 | CFM |  | 0
|  | 0 | Temp, deg. F |  | 0 | Enter Desired Height |  |  |  |  | Enter Width
|  | 0 | Humidity, Gr/Lb |  | 0 |  |  |  | Rectangular Duct Height (in) | 8 |  |  |  | Rectangular Duct Width (in) | 16
|  |  | Second Airstream |  |  | Results |  | rounded to nearest inch |  |  | Results |  |  | rounded to nearest inch
|  | 0 | CFM |  | 0 |  |  |  | Rectangular Duct Width (in) | 14 |  |  |  | Round Duct Diameter (in) | 13
|  | 0 | Temp, deg. F |  | 0
|  | 0 | Humidity, Gr/Lb |  | 0 | APPROXIMATE DYNAMIC |  |  |  |  | MAXIMUM RECOMMENDED
[6 empty] | LOSS COEFFICIENTS |  |  |  |  | SUPPLY VELOCITY
|  |  | Mixture Results | [10 empty] | Main Duct | Branch
|  | 0 | CFM |  | 0
|  | 0 | Temp, deg. F |  | 0 | [5 empty] | Residential |  |  | 900 fpm | 600 fpm
|  | 0 | Humidity, Gr/Lb |  | 0
[11 empty] | Commericial |  |  | 1,300 fpm | 900 fpm
[11 empty] | Industrial |  |  | 1,800 fpm | 1,000 fpm
® and ™ Trademarks of Bry-Air (Asia) Pvt. Ltd.
ALL INFORMATION ON THIS PAGE SHOULD BE VERIFIED BY A PROFESSIONAL ENGINEER AND IS PROVIDED FOR INFORMATIONAL USE ONLY
10793 St. Rt. 37 West Sunbury, Ohio 43074 Phone: 740.965.2974 Toll Free: 877.427.9247 Fax: 740.965.5470 Email: bryair1@bry-air.com www.bry-air.com
Total Environmental Conditioning Solutions™